## Slide 1: PowerPoint 12: Electrotechnical components
PowerPoint presentation
12. Building services engineering (BSE) systems
12.4 Electrotechnical principles of components

## Slide 2: Objectives
By the end of this session learners should be able to:
describe the wide variety of cables used in modern electrotechnical installations.
describe trunking, tray and busbar systems.

## Slide 3: Types of electrical cable
Steel wired armoured (SWA) cables.
Mineral insulated copper cables.
Fire performance P200 cables.
Solid core PVC insulated cables.
Multi-stranded PVC insulated cables.
Data multi-cored cables.

## Slide 4: Cable colour coding of conductors
Three phase circuits | 
Conductor designation | Conductor colour
Line 1 | Brown
Line 2 | Black
Line 3 | Grey
Neutral | Blue
Earth | Green/yellow
Single phase circuits | 
Conductor designation | Conductor colour
Line | Brown
Neutral | Blue
Earth | Green/yellow

## Slide 5: Choosing the right cable
Various cable types for wiring systems are in use, and the conditions of the surrounding environment will dictate what type will be selected.
Influential factors include:
moisture
temperature
possible impact damage
possible explosive atmosphere
flora (plants) and fauna (animals such as rats).

## Slide 6: Elements of a modern cable
Sheath (provides mechanical protection). Either thermoplastic (temperature range 0 to 70ºC), which can be reheated and reshaped, or thermosetting (temperature range 0 to 90ºC), which cannot be reheated.
Insulation (insulates against other conductors).
Conductor (typically copper or aluminium).

## Slide 7: PVC flat profile cable (twin and earth)
PVC (thermoplastic) flat profile cable is used in domestic wiring. It is cheap to manufacture, but has no earthing sleeving, so mechanical protection is low. If the thermoplastic insulation degrades, there is a risk of fire, so systems will need to be periodically upgraded (decommissioned/recommissioned).
Operating temperature is between 0 and 70ºC and the cable has a life of about 30 years.
Cable sizes above 1mm will have a smaller circuit protective conductor (cpc), which means resistance will be higher.
Notes: Image used with kind permission of CEF.

## Slide 8: XLPE and single-sheathed cables
Cross-linked polyethylene (XLPE) thermosetting cable is heat resistant and used as the final connection to an immersion heater. Its main advantage is a heat resistance of up to 90ºC. The downside is cost.
6491X single unsheathed PVC cable (commonly called ‘singles’) has no outer sheath, which means it is easier to wire inside conduits and trunking in commercial and industrial environments. The disadvantage of this type of cable is it cannot be used outside an enclosure because it does not have its own sheathing.
Three-core PVC white flexible cable is easy to install due to its flexibility. It is used for domestic lighting pendants, cabinet displays, table and standard lamps etc. High temperature versions are available, but none are very robust and so have a limited life.

## Slide 9: Flexible sheathed cables
Flexible cables are used mainly to connect appliances to hard-wired power outlets or fused spurs.
The illustration show a flexible cable with a heat resistant protective sheath, used for connecting appliances that generate heat (ie boilers and water heaters).
Notes: Photograph used with kind permission of TLC Electrical Supplies

## Slide 10: Steel-wired armoured cable
Steel-wired armoured (SWA) cable is suitable for electricity distribution underground and within buildings, running from switchgear to distribution boards.
The armour provides the main advantage of enhanced mechanical protection. The main disadvantage is weight, which is why containment systems such as ladders and trays are needed to support these cables. SWA cables are also expensive.
The illustration shows a three-phase and neutral cable with a cpc.
Notes: Image used with kind permission of CEF.

## Slide 11: SWA termination fittings
Brass connector clamps are used on the wire armour of the cable and compressed using an ‘olive’ (a compression ring).
The black cones shown are slipped onto the cable prior to termination, then pushed over the connector for insulation.
Two locknuts are placed between the metal of the containment and tightened to secure the connector.
Notes: Photograph used with kind permission of SWA.

## Slide 12: PVC SWA cable
PVC SWA cable has very high mechanical protection and is used in industrial, domestic and commercial sub-main supplies. The armour can negate the need for residual current device (RCD) protection. As pointed out earlier, the downside is that SWA cables are costly and very heavy.

## Slide 13: Mineral insulated copper cable
Mineral insulated copper cable (MICC) was used in fire protection and large boiler house control systems because of its high resistance to fire and heat (now superseded by FP200 cable). It is still used in applications suited to its combination of properties.
MICC has an outer sheathing of copper with bare copper conductors separated by compressed mineral insulation running through the sheathing.
A high level of competence is needed to install MICC cables.

## Slide 14: MICC

## Slide 15: MICC
The advantages of MICC are its very high operating temperature (>100ºC), long life and small sizing. It is very robust, and the internal gap between the conductors will be maintained even if the cable is flattened.
The weakest part of the cable is the gland, which must be kept airtight to prevent any moisture building up (the insulation material is magnesium oxide, which is hygroscopic).
MICC is expensive and fitting requires a range of specialised tools.

## Slide 16: FP200 cable
FP200 has now replaced MICC cable in fire alarm systems.
It is much easier to install and simpler to terminate.
When the cable is subjected to fire, the inner sheathing turns to glass and prevents the conductors from coming into contact, thereby maintaining the integrity of the alarm system.
It is heat resistant to 830ºC and less expensive than MICC, but not as long-lasting.

## Slide 17: Belden or data cables
Data or Belden cables are multi-cored and have small conductors designed to carry low voltages (data signals) from sensors to central hubs.
All the conductors within the sheath have a different colour code to assist termination.
They are used in building energy management (BEM) systems, computers, intruder and fire alarm systems and are ideal for information/data transfer.
They can be prone to interference and are extremely fiddly to terminate!

## Slide 18: Fibre-optic cables
Fibre-optic cables transmit light using a process known as total internal refraction. They allow very high speeds of data transfer and because they transmit light and not electricity they are generally safer.
They are not robust and therefore careful handling is needed to avoid internal damage.

## Slide 19: Cable containment systems
A wide range of cable containment systems is available to suit the needs of many system environments. For example:
steel conduit (black, galvanised, stainless steel)
plastic conduit (round and oval)
trunking (metal, plastic)
tray
basket
metal-clad busbar.

## Slide 20: Steel conduit
Steel conduit provides good protection from impact and environmental attack.
Steel conduits are available in black low carbon steel (LCS), galvanised LCS and stainless steel.
The tubing is threaded at the ends to facilitate connection to a variety of fittings and boxes.
Under current regulations, a cpc is installed in the conduit.
The diameter of the conduit dictates the number of conductors that can be safely installed.
Notes: Photo used with kind permission of Lasnek.

## Slide 21: Steel conduit
The advantages of steel conduit are its high level of mechanical protection and the fact that it can be used as a cpc.
The downsides are:
cost
weight (heavy)
the requirement of a former to bend the conduit
the possible need to galvanise for rust protection.
Notes: Photo used with kind permission of Lasnek.

## Slide 22: Plastic conduit
Plastic conduit is easier to install than metal and has a similar number of components available.
The tubing is glued into the fittings to make a secure joint.
It requires a large number of clip fixings to prevent sagging when subjected to heat.
Plastic conduit is ideal for domestic installations.

## Slide 23: PVC conduit
PVC conduit is easy to install, cheaper than metal alternatives and its property of non-conductivity means it is suitable for use in situations where direct contact is likely (eg where animals are involved). Heavy duty versions are available.
However, mechanical protection is limited, PVC conduit cannot be used as a cpc and bending must take place at room temperature to avoid cracking. If subjected to direct sunlight, PVC conduit may expand, therefore an expansion coupler is fitted at every 5m of its length.

## Slide 24: Metal trunking
Single compartment metal trunking can be used as the cpc, although this is not best practice, given that any ingress of dirt or corrosion can lead to higher values of cpc resistance. Metal trunking does provide excellent mechanical protection, and it is generally easier to add further cables to an existing run compared to a conduit.
To abide by the wiring regulations, wiring enclosures such as trunking and conduits should comply with a ratio of 45% cable to 55% air. This will minimise any cumulative heating effect.
Notes: Photo used with kind permission of Lasnek.

## Slide 25: Metal trunking
Metal trunking is an easy way of wiring several circuits, either fixed to walls or suspended at high level.
It is commonly used with strip lighting in large open spaces – factories and supermarkets, for example.
Suitable cables are flat PVC or single PVC insulated.
Where jointed to a fitting or coupled, an earth continuity wire is used to bridge the joint for safety.
Notes: Photo used with kind permission of Lasnek.

## Slide 26: Metal trunking
Metal trunking offers a high level of mechanical protection and can be used to separate emergency, Band I, and Band II systems to reduce electromagnetic interference.
It is easier to install extra cables than would be the case in a conduit, but this type of trunking is expensive, heavy and tricky to install. When single compartment metal trunking houses different voltage systems, then all the cables involved must be insulated to the highest voltage present.

## Slide 27: Multi-compartment metal trunking
Segregated compartments provide a means of isolating power and lighting circuits from data cables and limiting the number of conductors in contact with each other.
Multiple compartments means a separate uninterruptible power supply (UPS) circuit can be isolated from normal circuits.

## Slide 28: Plastic trunking
‘Mini trunking’ is an ideal way of installing surface-mounted hard wiring cable in domestic situations such as wiring in garages and basements, giving a tidy appearance.
It is usually screwed to the wall or ceiling but may also be fixed with adhesive strips.
Plastic trunking is useful to protect small cable runs. It is easy to clean, non-conductive and provides 50mm depth protection. Mechanical protection is limited, it cannot be used as the cpc and can look rather ugly and intrusive in a room.

## Slide 29: Plastic segregated dado trunking
Dado trunking is useful in open plan office spaces for distributing power for computers and other office equipment above desk height.
Power outlet sockets can be incorporated in the front cover (see the next slide).
Computer ‘clean’ ring mains can be separated from normal power and data cables using this trunking.

## Slide 30: Plastic dado trunking

## Slide 31: Metal cable trays
Cable trays are used in voids above ceilings or in service ducts below the floor. They are perforated for cooling purposes and strong enough to support SWA cables.
Cables can be laid along them conveniently and in large quantities for power distribution or data systems. The trays can be segregated (as shown) to separate different cable bundles. They have high levels of mechanical protection but are not fully enclosed.

## Slide 32: Metal cable baskets and cable ladders
Metal cable baskets are similar to cable trays but more lightweight and therefore easier to fit. They are a convenient way of identifying various circuits by eye. They are an effective way of supporting data and emergency cable systems and cheaper than other containment devices such as trays or ladders. Like cable ladders, they only offer medium levels of mechanical protection.
Cable ladders are strong, robust, and mainly used in overhead industrial environments to support SWA cables.

## Slide 33: Busbar systems
Advantages and disadvantages
Can supply very high levels of current but …
  maintenance schedule required to maintain all the mechanical connections
  not easy to incorporate extra circuits.
Busbar systems are normally used in industrial environments, when high amounts of current is required. A major disadvantage of busbar systems is that a high level of maintenance is required to ensure that all interconnections are clean and rust free.

## Slide 34: Busbar systems
SWA cables enter the busbar chamber using their termination fitting
the three-phase conductors are then bolted to the separate busbars, matching each phase and neutral for continuity.
Shorting two phases would give a 400V potential.
In a busbar system:
Notes: Busbar systems are normally used in industrial environments, when high amounts of current is required. A major disadvantage of busbar systems is that a high level of maintenance is required to ensure that all interconnections are clean and rust free.
Image source: Jim Brian Electrical Services.

## Slide 35
Any questions?