## Slide 1: PowerPoint 5: Commercial and industrial heating systems
PowerPoint presentation
12. Building services engineering (BSE) systems
12.1 Building services engineering systems

## Slide 2: Objectives
By the end of this session learners should be able to:
describe industrial and commercial heating systems and their main components
draw a typical system layout
explain the operation of such systems
discuss the advantages and disadvantages of different systems and components.

## Slide 3: Why heat your commercial space?
  Compared to domestic heating systems, industrial/commercial systems normally require greater capacity to cope with the larger spaces and multiple floors involved. Some industries also require their products to be maintained at a certain temperature.
  As with domestic dwellings, in addition to providing thermal comfort, heating a building can prevent surface condensation and mould growth, therefore inhibiting damage to surfaces and to the whole structure by preventing interstitial condensation.
  The types of system used in commercial and industrial buildings include two-pipe parallel return, two-pipe reverse return and pumped primary and secondary. Large installations often have multiple boilers to meet their heating needs. Underfloor heating is used in some contexts, and all these systems require a range of specific components.

## Slide 4: Two-pipe parallel return systems
    This type of system has two pipework networks – a flow and a return – to each heat emitter.
    Pipe sizes are based on the mass flow rate of the emitters. The largest diameter pipes go from and to the boiler(s).
    Progressing through the system, the flow pipes get smaller and the return pipes get progressively larger as they approach the boiler(s).
    The length and diameter of each pipe will determine the frictional resistance of each section ( the Pa/m of a pipe).
    The total resistance of the system determines the duty of the pumps.
    Each emitter will have a control valve and a lockshield valve to facilitate system balancing (when commissioning the system).

## Slide 5: Two-pipe parallel return system: direct return

## Slide 6: Plan of a two-pipe system in a multistorey building

## Slide 7: Two-pipe reverse return systems
This type of system is commonly used in small commercial contexts. Here the two-pipe parallel return has the flow and return pipes flowing in the same direction.
Because of the configuration of the system, all the heat emitters are the same distance from the boiler(s) – therefore there is no requirement for balancing because the system ‘self balances’, and because the flow and return pipes are of equal length, even in a large building the radiators will warm up over an even time period.
Substantially more pipework is needed, in turn increasing the pump duty required.
Notes: Because the flow and return pipes are equal lengths, in a big building, each radiator would warm up at an even time period.

## Slide 8: Two-pipe reverse return system

## Slide 9: Pumped primary/pumped secondary systems
Multiple boiler installations often incorporate low loss headers with the main purpose of maintaining water velocity, enabling independent operation of primary and secondary circuits.
Low loss headers also allow the inclusion of independent balanced pump circuits and the use of mixed heat emitters in the whole heating system.
Notes: Photograph used with kind permission of Smiths Heating Services Ltd.

## Slide 10: Pumped primary/pumped secondary systems
The illustration on the next slide shows a low loss header system.
    The low loss header is a large diameter pipe which is connected to the boiler(s). Because of its large diameter, the primary water flows through it very slowly compared to the distribution pipe, therefore there is a low resistance to flow.
    Secondary circuits are then connected to the header with a pump to circulate the secondary water.
    Several secondary circuits can be connected to serve different zones of the heating system.
    Compensated circuits can also be installed, allowing the building to respond to outside variations in temperature.

## Slide 11: Low loss header system
Notes: Multiple boiler installations or larger systems often incorporate low loss headers with the main purpose of maintaining water velocity, enabling independent operation of primary and secondary circuits.
Low loss headers also allow the inclusion of independent balanced pump circuits and the use of mixed heat emitters in the whole heating system.

## Slide 12: Multiple boiler plantroom installations
Large plantrooms will have several small boilers rather than one large one.
    These units are cheaper to buy and replace, and an individual boiler can be replaced easily without disrupting the system.
    A boiler sequencer can be installed to bring the boilers online when more heat is required. A temperature sensor in the primary flow informs the sequencer when more or less heat is required.
    The boilers can be programmed to ‘share the duty’, thus prolonging their life expectancy.
    Secondary circuits are connected to external and internal temperature sensors, thereby controlling the temperature of the heating circuits.

## Slide 13: Multiple boiler plantroom installation and boiler sequencer

## Slide 14: Multiple boiler plantroom with low loss header
Here you can see the individual boiler connections to the primary flow and return pipes.
An in-line twin-duty and standby pump set with intelligent motor heads driving multi-stage centrifugal impellers is also visible.

## Slide 15: Small plantroom control panel
Plantroom control panels have all the elements of the plantroom (boiler burners, pumps, motorised valves and temperature sensors) wired into them.
Control panels have built-in time switches and external weather compensators as required.
Each element has indicator lights to show its status. Green lights indicate normal running, red lights indicate a fault.
Where duty and standby pumps are utilised, automatic switching can be achieved to maintain system pumping.

## Slide 16: Compensated heating control
In this system the temperature of the heating zone heat emitters rises or falls to compensate for external temperatures. The system controls the mix of return water and hot water from the boiler. When the system first starts to operate the external temperature will be at its coolest.
As the temperature rises outside, less heat will be required internally. By mixing the two inlets to the three-port valve, the emitter temperature cools and less heat is transferred to the building. Three sensors regulate the mix.

## Slide 17: Constant volume/variable temperature compensated heating circuit
This system is designed to control the temperature passing through the heat emitters to compensate for external environmental conditions.
The warmer a room gets, the more the temperature of the water in the system is reduced by mixing the flow and return waters.
The volume of water flowing remains the same because the system will have been commissioned for that amount water to flow through it.

## Slide 18: Constant temperature/variable volume circuit
An alternative way of using a three-port valve is to divert fresh water away from the load, thus reducing the amount of energy available for transfer.
Examples where this principle is used are a hot water storage calorifier or a heater battery in an air handling unit.
The amount of volume diverted is controlled by a thermostat.
Note the position of the pump in the two examples compared to the previous mixing set-up.

## Slide 19: Pumps and valves
When used as diverting valves, port AB functions as the inlet, while ports A and B function as the outlets. When used as mixing valves, fluids from inlet ports A and B are mixed inside the valve body and expelled through port AB.
Three-port valves are used to either mix or divert flow in hydronic heating systems. A motorised head motor moves the actuator to control the flow of liquid when the sensors indicate a change is required.
Three-port motorised mixing and diverting valves

## Slide 20: Pumps and valves
This valve is normally connected to the flow pipe entering the heat emitter.
The ambient temperature is sensed by a sensor containing an alcohol vapour mixture which expands or contracts to move the valve in relation to the valve seating, thereby regulating the flow of water to the heat emitter.
Once set by the end user it automatically controls output.
Thermostatic radiator valve

## Slide 21: Pumps and valves
Automatic air valves are installed at the highest points in the pipework, usually on top of an air bottle used to trap any air circulating in the pipes.
Air in pipework affects the performance of the system and causes corrosion of the pipes.
A bleed pipe is taken off the top to either a drain or an outside wall.
Automatic air valve

## Slide 22: Pumps and valves
This in-line valve is used by commissioning engineers to set the system to work.
The two binder points measure a pressure differential across an orifice.
Two probes from a digital manometer are inserted in the top of the points.
The valve is set to match the commissioning values. Once set the valve can then be used to isolate the unit. When the valve is reopened the same resistance will continue as set.
Double regulating valve with binder test points
Notes: Photograph used with kind permission of Frese.

## Slide 23: Pumps and valves
The pump motor illustrated has intelligent controllers attached which adjust the energy consumed by the motors by reducing the flow rate when the system requires less water.
The pump set also has an automatic changeover if one pump fails.
Twin centrifugal sets can be connected to a building energy management (BEM) system.
In-line twin centrifugal pump set
Notes: Photograph used with kind permission of Wilo.

## Slide 24: Underfloor heating systems
Underfloor heating is now one of the most widely used systems for heating domestic and commercial properties. Its growing popularity is due to benefits such as comfort, economy, flexibility and being being virtually maintenance free. A minimum of 65ºC is required at the manifold (shown here), which is then blended from the return to give approximately 55ºC (40ºC can be used via a ground source).
See PowerPoint 4 for layout and description.

## Slide 25: Pipework
Building pipework systems onsite is very labour intensive and costly. There is typically a 30% waste of materials whereas prefabricating units in a factory cuts waste down to 3% and labour costs are also greatly reduced.
Prefabricated pipework (built offsite)
The units are fixed in place by pipefitters and jointed onsite. Before commissioning can take place the entire system is flushed out and pressure tested. All the units are pre-tested in the factory and then insulated. The picture shows prefabricated pipes ready for assembly.
Notes: Photograph used with kind permission of Offsite Engineering Solutions.

## Slide 26: Components in prefabricated commissioning sets
Commissioning sets produced offsite do not just include pipework but other components such as double regulating valves, isolating valves and pressure differential bypass valves.
Prefabricated sets can also provide all the items that would typically be in a plantroom.
Notes: Photograph used with kind permission of Offsite Engineering Solutions.

## Slide 27: Pipework
Copper piping is fixed onsite because the jointing method requires a level of skill which is beyond factory workers. The use of copper is dictated by the design engineer’s preference.
Copper pipework (built onsite)

## Slide 28: Balancing the system
When a system is designed, the engineer responsible will have calculated all the flow rates and pressure loss of the pipework.
The commissioning engineers will have the data for each commissioning set, and by attaching a digital manometer to the two test points of each set they can adjust the regulating valves to give the required flow rate and pressure drop across the valves. Sets of this type are not used in domestic heating systems.

## Slide 29: Heat emitters
Radiators are constructed from pressed steel panels welded together.
They are essentially either single panels with a convection grid welded to the rear, or double panels with one or two grids attached.
Radiators are used in smaller spaces either singly or in multiple, to match requirements.

## Slide 30: Heat emitters
Fan convectors are used in large spaces, for instance school workshops, meeting rooms, assembly rooms etc.
They will heat a space faster than traditional convector panels.
They are controlled by a room thermostat and a low-limit thermostat.

## Slide 31: Heat emitters
Unit heaters are designed for large heat outputs and are generally used in factories and large spaces where noise is not a factor.
A finned heat exchanger is connected to the flow and return pipework and a fan mounted at the rear of the unit recirculates room air across the exchanger.
Louvres on the outlet are used to direct the airflow where required.
Notes: Photograph used with kind permission of Raptor Supplies.

## Slide 32: Heat emitters
Radiant heat emitters are fitted in the ceiling, and are often used in hospitals and medical centres as they free up wall space for shelving and equipment.
They form part of the finished ceiling and consist of pipe coils attached to its surface.
Notes: Photograph used with kind permission of SPC.

## Slide 33
Any questions?