12: Building Services Engineering (BSE) systems

# Worksheet 4: Tightness testing (tutor)

Tightness testing is carried out to ensure that domestic gas pipework is safe for use, or continued use. The process tests for leaks in the installation.

You have been asked to give a toolbox talk about how to carry out a tightness test for new gas installation pipework.

Either individually or in small groups, write down the process you would follow. If you are unsure of the process, ask your tutor to refresh your knowledge.

Nominate a speaker(s) from the group to present the process step-by-step to the rest of the class.

Learners should cover the following steps.

- The pipework should be charged with air to 20–21mbar with a manometer connected to a test nipple.

- The pipework should stand for one minute to allow for temperature stabilisation.

- Check the gauge pressure.

- Top up pressure to 20mbar and leave to stand for two minutes.

- If after two minutes the pressure drops below 20mbar, this indicates there is a leak.

- The leak should be traced and rectified.

- Repeat test from step 1 to 6.

- When no pressure drop occurs the pipework is sound and ready for the gas.

Check for understanding and ensure that learners have a full knowledge of the process.

To stretch/challenge, you could ask learners to compare this new installation process with the process for existing pipework and identify the differences, or split the class into two groups to cover both processes.